## Sheet1
Standard Inverse Time Overcurrent Relay (SI) : Calculation for 22 kV system.
Bus | 1 | 2 | 3 | 4
Maximum Fault Currents (3 phase fault) | 3175.4265 | 1411.3007 | 907.2647 | 668.5108
Minimum Fault Currents (L-L fault) | 2750 | 1222.2222 | 785.7143 | 578.9474
Max.Fault Current (A) (ต้นสายส่ง) | 3175.4265 | 1411.3007 | 907.2647
Min.Fault Current (A) (ปลายสายส่ง) | 1222.2222 | 785.7143 | 578.9474
Coordinated Fault Current (A) | 1411.3007 | 907.2647
1/3 of Min. Fault Current (A) (CT primary) | 407.4074 | 261.9048 | 192.9825
Pick up Current that relay must see (A) (CT primary) | 261.9048 | 192.9825
CT ratio ( /5 A) | 300 | 200 | 200
1/3 of Min. Fault Current to relay (A) (CT secondary) | 6.7901 | 6.5476 | 4.8246
Pick up Current that relay must see (A) (CT secondary) | 4.3651 | 4.8246 | 4.8246
Tap Setting (A) Relay pick up current : Ip | 4.25 | 4.75 | 4.75
Coordinated Fault Current (A) (CT secondary) | 23.5217 | 22.6816
Coordinated Fault current (p.u.) (CT secondary เทียบกับ Tap setting | 7.4279 | 4.7751
Prefered Delay Time Coordination (sec.) | 0.87499 | 0.74078
Actual Delay Time When See Max. Fault (From relay curve) |  | 0.57499 | 0.44078
Time Multiplier Setting | 0.21758 | 0.16806 | 0.1